# Overpressure Protection

Four basic methods of overpressure protection

- Relief Valve

- Monitor Regulator (Worker/Monitor)

- Overpressure Shutoff

- Series Regulation

## Relief Valves

- Internal Relief Valve (IRV)

- External Relief Valve (Stand Alone)

## Sizing Relief Valves

Internal Relief Valve (IRV)

- Choose the model, body size, and orifice size of a pressure reducing regulator with an IRV.

- Determine the maximum inlet pressure placed on the regulator.

- Check the relief characteristics using the maximum pressure to insure the downstream build pressure will not exceed allowable limits.

- If limits are exceeded, consider a smaller orifice, a different (larger diaphragm) regulator, or an additional form of overpressure protection.

Stand Alone Relief Valves (External Relief Valves)

- Determine the volume of gas passed by the failed pressure reducing regulator under maximum regulator flow conditions (maximum inlet pressure, minimum outlet pressure).

- Determine a margin of safety to be used to oversize the relief valve (10%?).

- Choose a relief valve that will allow this amount of gas to vent to atmosphere.

- Use the relief set pressure as the inlet pressure to the relief valve and 0 psig as the outlet pressure to determine the capacity of the relief valve.

- Be aware of possible build pressure issues.

Full Open Regulator capacity:

- For sizing downstream relief valves, use absolute pressures in the following formulas to determine the regulator full open capacity.

- Critical Flow if P2 / P1 ≤ 0.5

- Sub-Critical Flow if P2 / P1 > 0.5

Sub-Critical Flow Equation			Critical Flow Equation

Q=0.5CP1maxG

Qmax=CP2min×hG

Where,

Q - Full open capacity of the regulator

C - Orifice Constant

P1 - Inlet absolute pressure

P2 - Outlet absolute pressure

h - Differential pressure (P1 -  P2)

G - Specific Gravity of the Gas

Relief Valve Vents

- Venting must be considered when using a relief valve for overpressure protection.

- Protect vents from bugs and water with caps and/or screens.

- Do not pipe two regulators/relief valves into one vent pipe.

- Vent into a safe area.

- Vent line should be as short and straight as possible.

- Size relief vent (blow off stack) adequately or performance will be jeopardized.

## Relief Valve Advantages

- Considered the most reliable type of overpressure protection.

- Imposes no reduction in capacity to the system.

- Acts as an alarm (smell and noise) when relieving.

- Low associated costs (IRV).

- Relief valve resets itself once the overpressure condition is resolved.

### Relief Valve Disadvantages

- Vents gas to atmosphere - creates a possible hazard.

- May create a public relations problem due to the noise associated with its operation.

- Each station must be sized individually.

## Monitor Regulators

- Monitor Regulator - A regulator that acts as a safety for a pressure reducing regulator.

- The controlled pressure that is normally monitored is the outlet pressure of a pressure-reducing regulator.

- The monitor regulator pressure is set slightly higher than that of the reducing regulator, so that it will not control pressure unless the pressure increases to its outlet set point.

- Monitor will not take over control unless worker has failed in an open position.

Monitor Regulator Advantages

- Protects against overpressure condition without blowing the excess gas to atmosphere.

- Prevents the gas system from being shut down unexpectedly.

- No public relations problems are created because the gas is contained.

- Testing is relatively easy and safe.

#### Monitor Regulator Disadvantages

- Additional expenses associated with two regulators and piping requirements.

- Reductions of station capacity due to the pressure drop across the monitor regulator (the worker/monitor set has  71% of the capacity of a single regulator).

Overpressure Shutoff

- Designed to trip and provide positive shutoff to the system in the event the pressure reducing regulator experiences a failure.

- This method is generally applied to single user installations.

Two types of overpressure shutoffs are available.

- Integral

- Non-integral

##### Overpressure Shutoff Advantages

- Safety is assured by containing the upstream pressure.

- No public relations problems or hazards from venting gas to atmosphere.

##### Overpressure Shutoff Disadvantages

- The customer may be shutoff due to a minor problem that would have been taken care of by an internal relief valve.

- When the shutoff trips, all downstream equipment must be re-lit.

- Shutoff may trip under no flow periods due to temperature rising the outlet pressure.

Series Regulation

- Uses two regulators.

- The upstream regulator maintains an inlet pressure to the second that is equal to or less than the maximum allowable working pressure (MAOP) of the downstream equipment.

- The emergency outlet pressure rating of the downstream regulator must be high enough to withstand the full inlet pressure.

###### Series Regulation Advantages

- One of the simplest systems that will provide overpressure protection by containment.

- No public relations problems or hazards from venting gas to atmosphere.

#### Series Regulation Disadvantages

- Maintaining tight control of the outlet pressure in the event that the downstream regulator should fail.

- Additional expenses associated with two regulators.

## Overprotection Advantages and Disadvantages

Basic Method			Relief       Monitor       Series       Shutoff

Keeps customer on line	    Y	         Y		   Y	              N

Public relations problems	    Y	         N		   N	              N

Manual resetting required    	    N	         N		   N	              Y

Reduces capacity		    N	         Y		   Y	              N

Demands “emergency” action   Y	         N		   N	          Y