Regulator Troubleshooting (Fault Finding)

| #### Problem | ### Possible Cause | Possible Cure |
| --- | --- | --- |
| Failure to hold set point or Outlet pressure drops off. | Lack of capacity in regulator. | Check technical data and operating conditions and compare against the connected load. Has connected load changed? |
|  | Pressure gauge | Check pressure gauge and ensure that it is positioned in the right location. |
|  | Shipping plugs or screws not removed. | Inspect regulator ports and vents for shipping plugs. Inspect inside of regulator to ensure orifice is clear. |
|  | Regulator not properly set | Verify set point pressure and ensuring to set at the proper flow rate. |
|  | Pressure elevation effects | Check inlet pressures under varying flow rates. Does the inlet drop off under high flows? Is the inlet piping sized correctly? Is the outlet pipe sized correctly? |
|  | Block valves not fully open. | Verify position of all valves. |
|  | Debris in Filters/Strainers | Check differential pressure across any filters or strainers to ensure they are not obstructed. Read pressure directly in inlet of regulator. Are inlet pressures steady over a variety of flow rates? |
|  | Obstructions in pipeline. | Inspect inside of pipe and clear any obstructions. |
|  | Regulator moving parts binding. | Inspect internal moving parts for binds or friction. Internal parts should move freely. |
| Failure to lock-up or shut off | Damage to seat, seat disc, or orifice. | Inspect and replace if needed. Remove any debris that may be preventing full closure. |
|  | Overpressure of diaphragm. | Check for damaged or buckled diaphragm plate. |
|  | Leakage around orifice. | Check and apply sealant to orifice threads. Ensure unit is assembled properly. |
|  | Defective body casting. Leakage between inlet and outlet chambers. | Inspect and replace if necessary. |
|  | Vent plugged. | Inspect and clean vent openings. |
|  | Spring coil bound | Check for lock-up at lower settings. |
|  | Lock-up experience in monitor lock-up | Are higher pressures coming from a monitor situation where downstream pressures may be coming from a different source? Is monitor setting higher or set tool close to primary? |

| No control at all | Valve Seat missing | Check for placement and possible damage |
| --- | --- | --- |
|  | Orifice missing | Check for placement and possible damage |
|  | Control/Loading line blocked or not connected | Check |
|  | Pilot supply insufficient | Check |
|  | Inlet valve closed | Confirm valve is open |
|  | Control valve closed | Confirm control or pilot supply valves are open |
|  | Outlet valve closed | Confirm valve is open |
|  | Incorrect Spring for application | Check spring range to ensure it is right for the application |
|  | Diaphragm ruptured | Check and replace if necessary |
|  | Regulator installed backwards | Check flow arrow on valve head to ensure it is pointed in the proper direction |
|  | Control line incorrectly positioned | Check where all control lines are connected and verify proper location. The rule of thumb is 5 nominal pipe diameters downstream of the regulator. |
|  | Moisture in diaphragm chamber | Clean and prevent moisture increases by use of a filter. Mount regulator to allow for self-draining. |
| Vibration or humming with no drift from set point | Vent line diameter or length restrictive | Vents must be large enough to allow for air displacement as diaphragm moves. |
|  | Two vents from separate regulators tied together | Air movement from one diaphragm chamber may effect other regulator. |
|  | Loose adjusting cap or seal cap | Check, replace, or tighten as necessary |
|  | Incorrect location of regulator relative to apparatus (i.e. rotary meter, compressor) | Rapid load changes downstream may effect regulator stability. |
|  | Too tight of spring | Check spring range and select next higher range if possible. |
| Slow drift from set point | Oversized orifice for inlet pressure (inlet pressure effect) | Check orifice to ensure it is sized properly for the load. |
|  | Binding/Friction in moving parts | Check to ensure free movement of parts. |
|  | Moisture in control line freezing (short periods of time) | Remove condensates or add heat to prevent freezing. |

| Sluggishness or generally poor control or regulator | Binding/Friction stiffness in diaphragm | Inspect diaphragm for recommended operating temperature. Check for free movement. |
| --- | --- | --- |
|  | Control line partially blocked or incorrectly sized | Check, clean and blow through |
|  | Intermittent blockage in main piping system (i.e. water, plugged filter/strainer) | Remove and ensure clean and clear supply and discharge piping |
| Pulsating, humming, chattering, instability | Incorrect size or type of regulator. | Check sizing and model selection for the operating conditions. |
|  | Incorrect location of control line or undersized control line | Check and get away from areas of turbulence or high gas velocities. |
|  | Undersized vent line | Increase size of vent line at regulator. Compliment of Roger |
|  | Interaction between adjacent apparatus | Check and adjust as needed. |
|  | Poor downstream piping design - results in severe turbulence or back pressure against the regulator | Review design and make appropriate changes. |
| Leakage from diaphragm vent | Hole in diaphragm | Check diaphragm for holes, cuts, or tears. |
|  | Internal relief operating | Check inlet and outlet pressures. Is outlet pressure high enough to open relief? Investigate cause. Reset relief set point. Check for debris under seat disc. |
|  | Internal relief improperly set | Check and reset if necessary. |
|  | Diaphragm center bolt leaking | Reseal or replace diaphragm as required. |
|  | Internal relief not assembled correctly | Check, disassembly and repair as necessary. |